## SDR 41 - SDR 26 - SDR 17
PE Pipes for Water Supply
Dimensions & Working Pressure Table(PE100)
This table lists pipe dimensions and pressure classes for potable water supply systems to support correct selection and installation.
Nominal Outside Diameter (mm) | SDR 41 S20 |  |  | SDR 26 S12.5 |  |  | SDR 17 S8
| PN 4 |  | Code | PN 6.3 |  | Code | PN 10 |  | Code
| Wall thickness mm | Weight kg/m |  | Wall thickness mm | Weight kg/m |  | Wall thickness mm | Weight kg/m
16 | - | - | - | - | - | - | - | - | -
20 | - | - | - | - | - | - | - | - | -
25 | - | - | - | - | - | - | 1.8 | 0.137 | SAP13010025100
32 | - | - | - | - | - | - | 1.9 | 0.187 | SAP13010032100
40 | - | - | - | 1.8 | 0.227 | SAP13063040100 | 2.4 | 0.295 | SAP13010040100
50 | - | - | - | 2 | 0.314 | SAP13063050100 | 3 | 0.453 | SAP13010050100
63 | 1.8 | 0.346 | SAP13004063100 | 2.5 | 0.494 | SAP13063063100 | 3.8 | 0.721 | SAP13010063100
75 | 1.9 | 0.457 | SAP13004075100 | 2.9 | 0.675 | SAP13063075100 | 4.5 | 1.02 | SAP13010075100
90 | 2.2 | 0.643 | SAP13004090100 | 3.5 | 0.978 | SAP13063090100 | 5.4 | 1.46 | SAP13010090100
110 | 2.7 | 0.943 | SAP13004110100 | 4.2 | 1.43 | SAP13063110100 | 6.6 | 2.17 | SAP13010110100
125 | 3.1 | 1.23 | SAP13004125100 | 4.8 | 1.84 | SAP13063125100 | 7.4 | 2.76 | SAP13010125100
140 | 3.5 | 1.54 | SAP13004140012 | 5.4 | 2.32 | SAP13063140012 | 8.3 | 3.46 | SAP13010140012
160 | 4 | 2 | SAP13004160012 | 6.2 | 3.04 | SAP13063160012 | 9.5 | 4.52 | SAP13010160012
180 | 4.4 | 2.49 | SAP13004180012 | 6.9 | 3.79 | SAP13063180012 | 10.7 | 5.71 | SAP13010180012
200 | 4.9 | 3.05 | SAP13004200012 | 7.7 | 4.69 | SAP13063200012 | 11.9 | 7.05 | SAP13010200012
225 | 5.5 | 3.86 | SAP13004225012 | 8.6 | 5.89 | SAP13063225012 | 13.4 | 8.93 | SAP13010225012
250 | 6.2 | 4.83 | SAP13004250012 | 9.6 | 7.3 | SAP13063250012 | 14.8 | 11 | SAP13010250012
280 | 6.9 | 5.98 | SAP13004280012 | 10.7 | 9.1 | SAP13063280012 | 16.6 | 13.7 | SAP13010280012
315 | 7.7 | 7.52 | SAP13004315012 | 12.1 | 11.6 | SAP13063315012 | 18.7 | 17.4 | SAP13010315012

## SDR 13.6 - SDR 11 - SDR 9
PE Pipes for Water Supply
Dimensions & Working Pressure Table(PE100)
This table lists pipe dimensions and pressure classes for potable water supply systems to support correct selection and installation.
Nominal Outside Diameter (mm) | SDR 13.6 S6.3 |  |  | SDR 11 S5 |  |  | SDR 9 S4
| PN 12.5 |  | Code | PN 16 |  | Code | PN 20 |  | Code
| Wall thickness mm | Weight kg/m |  | Wall thickness mm | Weight kg/m |  | Wall thickness mm | Weight kg/m
16 | - | - | - | - | - | - | 1.8 | 0.084 | SAP13020016100
20 | 1.8 | 0.107 | SAP13125020100 | 1.9 | 0.112 | SAP13016020100 | 2.3 | 0.133 | SAP13020020100
25 | 1.9 | 0.144 | SAP13125025100 | 2.3 | 0.171 | SAP13016025100 | 2.8 | 0.2 | SAP13020025100
32 | 2.4 | 0.232 | SAP13125032100 | 2.9 | 0.272 | SAP13016032100 | 3.6 | 0.327 | SAP13020032100
40 | 3 | 0.356 | SAP13125040100 | 3.7 | 0.43 | SAP13016040100 | 4.5 | 0.509 | SAP13020040100
50 | 3.7 | 0.549 | SAP13125050100 | 4.6 | 0.666 | SAP13016050100 | 5.6 | 0.788 | SAP13020050100
63 | 4.7 | 0.673 | SAP13125063100 | 5.8 | 1.05 | SAP13016063100 | 7.1 | 1.26 | SAP13020063100
75 | 5.6 | 1.24 | SAP13125075100 | 6.8 | 1.47 | SAP13016075100 | 8.4 | 1.76 | SAP13020075100
90 | 6.7 | 1.77 | SAP13125090100 | 8.2 | 2.12 | SAP13016090100 | 10.1 | 2.54 | SAP13020090100
110 | 8.1 | 2.62 | SAP13125110100 | 10 | 3.14 | SAP13016110100 | 12.3 | 3.78 | SAP13020110100
125 | 9.2 | 3.37 | SAP13125125100 | 11.4 | 4.08 | SAP13016125100 | 14 | 4.87 | SAP13020125100
140 | 10.3 | 4.22 | SAP13125140012 | 12.7 | 5.08 | SAP13016140012 | 15.7 | 6.11 | SAP13020140012
160 | 11.8 | 5.5 | SAP13125160012 | 14.6 | 6.67 | SAP13016160012 | 17.9 | 7.96 | SAP13020160012
180 | 13.3 | 6.98 | SAP13125180012 | 16.4 | 8.42 | SAP13016180012 | 20.1 | 10.1 | SAP13020180012
200 | 14.7 | 8.56 | SAP13125200012 | 18.2 | 10.4 | SAP13016200012 | 22.4 | 12.4 | SAP13020200012
225 | 16.6 | 10.9 | SAP13125225012 | 20.5 | 13.1 | SAP13016225012 | 25.2 | 15.8 | SAP13020225012
250 | 18.4 | 13.4 | SAP13125250012 | 22.7 | 16.2 | SAP13016250012 | 27.9 | 19.4 | SAP13020250012
280 | 20.6 | 16.8 | SAP13125280012 | 25.4 | 20.3 | SAP13016280012 | 31.3 | 24.3 | SAP13020280012
315 | 23.2 | 21.2 | SAP13125315012 | 28.6 | 25.6 | SAP13016315012 | 35.2 | 30.8 | SAP13020315012